SILVerify IEC 61508 / IEC 61511 SIL Verification Report Hardware Reliability Verification — Low Demand Mode

| Project | Sample — High Pressure Trip System |
| --- | --- |
| Client | Acme Chemicals Ltd |
| Site | North Plant — Unit 5 |
| Engineer | Sample Engineer |
| Reference | SAM-001 |
| Standard | IEC 61511 |
| Date | 22 March 2026 |
| Revision | Rev 0 |

| Reference | Revision | Date | Status |
| --- | --- | --- | --- |
| SAM-001 | Rev 0 | 22 March 2026 | Issued |

IMPORTANT — SCOPE OF THIS DOCUMENT This report presents the results of a SIL verification calculation covering random hardware reliability only (PFDavg). It does not constitute a complete functional safety assessment. Systematic capability of SIF elements must be assessed separately per IEC 61511 Clause 11.9. See Section 9 for full scope statement.

Table of Contents

1. Executive Summary	1

2. SIF Descriptions	1

SIF-001: High Pressure Trip	1

3. Architecture	1

SIF-001	1

4. Failure Data	1

SIF-001	1

Sensors	1

Logic Solver	1

Final Elements	1

5. UPM / CCF Assessment	1

SIF-001	1

Sensors	1

Logic Solver	1

Final Elements	1

6. Calculations	1

SIF-001	1

Sensors (2oo3)	1

Logic Solver (1oo2)	1

Final Elements (1oo2)	1

7. Results	1

SIF-001	1

8. Architectural Constraint (IEC 61508 Route 1H)	1

SIF-001	1

9. Systematic Capability Assessment	1

SIF-001	1

Subsystem SC Summary	1

10. Assumptions and Limitations	1

11. Scope of This Verification	1

12. Conclusion	1

SIF-001	1

THREE-BARRIER VERIFICATION SUMMARY	1

# 1. Executive Summary

| SIF Tag | SIF Name | Target SIL | Achieved SIL | PFDavg | Result |
| --- | --- | --- | --- | --- | --- |
| SIF-001 | High Pressure Trip | 2 | SIL 2 — Hardware | 2.24 × 10-3 | PASS |

Achieved SIL covers random hardware reliability (PFDavg) only. Systematic capability assessment required separately per IEC 61511 Clause 11.9.

# 2. SIF Descriptions

## SIF-001: High Pressure Trip

| Field | Value |
| --- | --- |
| SIF Tag | SIF-001 |
| SIF Name | High Pressure Trip |
| Description | Emergency shutdown of reactor feed on high pressure to prevent overpressure and potential vessel rupture. |
| Hazard | Reactor overpressure leading to loss of containment of hazardous materials. |
| Demand Mode | Low Demand |
| Target SIL | 2 |
| Mission Time LT | 87,600 hours (10.0 years) |

# 3. Architecture

## SIF-001

| Subsystem | Architecture | Channels |
| --- | --- | --- |
| Sensors | 2oo3 | 3 |
| Logic Solver | 1oo2 | 2 |
| Final Elements | 1oo2 | 2 |

# 4. Failure Data

The following table presents the reliability input data for all channels. All values as entered by the engineer of record.

## SIF-001

### Sensors

Table A — Reliability Parameters

| Instrument Tag | λD (failures/hr) | DC (%) | PTC (%) | TI (hrs) | MTTR (hrs) |
| --- | --- | --- | --- | --- | --- |
| PT-101A | 3.00 × 10-6 | 65% | 90% | 8,760 | 8 |
| PT-101B | 3.00 × 10-6 | 65% | 90% | 8,760 | 8 |
| PT-101C | 3.00 × 10-6 | 65% | 90% | 8,760 | 8 |

Table B — Data Traceability

| Instrument Tag | Data Source | Device Reference | Verified By | Verification Basis |
| --- | --- | --- | --- | --- |
| PT-101A | FARADIP Issue 4 | Table 3.1 — Differential Pressure Transmitter | J. Smith, Lead FSE | Certified Database |
| PT-101B | FARADIP Issue 4 | Table 3.1 — Differential Pressure Transmitter | J. Smith, Lead FSE | Certified Database |
| PT-101C | FARADIP Issue 4 | Table 3.1 — Differential Pressure Transmitter | J. Smith, Lead FSE | Certified Database |

### Logic Solver

Table A — Reliability Parameters

| Instrument Tag | λD (failures/hr) | DC (%) | PTC (%) | TI (hrs) | MTTR (hrs) |
| --- | --- | --- | --- | --- | --- |
| LS-101A | 7.10 × 10-8 | 99% | 100% | 8,760 | 8 |
| LS-101B | 7.10 × 10-8 | 99% | 100% | 8,760 | 8 |

Table B — Data Traceability

| Instrument Tag | Data Source | Device Reference | Verified By | Verification Basis |
| --- | --- | --- | --- | --- |
| LS-101A | Exida SERH | SERH 7.20 — Siemens S7-300 PLC | J. Smith, Lead FSE | Certified Database |
| LS-101B | Exida SERH | SERH 7.20 — Siemens S7-300 PLC | J. Smith, Lead FSE | Certified Database |

### Final Elements

Table A — Reliability Parameters

| Instrument Tag | λD (failures/hr) | DC (%) | PTC (%) | TI (hrs) | MTTR (hrs) |
| --- | --- | --- | --- | --- | --- |
| XV-101A | 5.00 × 10-7 | 0% | 85% | 8,760 | 8 |
| XV-101B | 5.00 × 10-7 | 0% | 85% | 8,760 | 8 |

Table B — Data Traceability

| Instrument Tag | Data Source | Device Reference | Verified By | Verification Basis |
| --- | --- | --- | --- | --- |
| XV-101A | Manufacturer FMEDA | FMEDA Report Rev B — XV-101 Actuated Ball Valve | J. Smith, Lead FSE | Certified Database |
| XV-101B | Manufacturer FMEDA | FMEDA Report Rev B — XV-101 Actuated Ball Valve | J. Smith, Lead FSE | Certified Database |

# 5. UPM / CCF Assessment

Common cause failure (CCF) is assessed using the Unified Partial Method (UPM) for redundant subsystems. The beta factor represents the fraction of dangerous failures attributable to common cause events.

## SIF-001

### Sensors

Beta source: manual, Beta used: 0.1

### Logic Solver

Beta source: manual, Beta used: 0.02

### Final Elements

Beta source: manual, Beta used: 0.1

Beta factors derived from UPM represent a structured engineering judgement consistent with IEC 61508 guidance. They are not statistically derived values. Beta derivation and justification should be subject to independent review for SIL 2 and above claims.

# 6. Calculations

All calculations use the simplified equations from IEC 61508-6 Annex B for low-demand mode. Per-channel intermediate values are shown for full traceability.

## SIF-001

### Sensors (2oo3)

| Instrument Tag | λD | DC | PTC | TI (hrs) | LT (hrs) | λDU | λDD | PFD_ch_UD | PFD_ch_DD | PFD_ch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PT-101A | 3.00 × 10-6 | 65% | 90% | 8,760 | 87,600 | 1.05 × 10-6 | 1.95 × 10-6 | 8.74 × 10-3 | 1.56 × 10-5 | 8.75 × 10-3 |
| PT-101B | 3.00 × 10-6 | 65% | 90% | 8,760 | 87,600 | 1.05 × 10-6 | 1.95 × 10-6 | 8.74 × 10-3 | 1.56 × 10-5 | 8.75 × 10-3 |
| PT-101C | 3.00 × 10-6 | 65% | 90% | 8,760 | 87,600 | 1.05 × 10-6 | 1.95 × 10-6 | 8.74 × 10-3 | 1.56 × 10-5 | 8.75 × 10-3 |

PT-101A: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (1.05 × 10-6/2) × [0.90×8760 + 0.10×87600] = 8.74 × 10-3

PT-101B: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (1.05 × 10-6/2) × [0.90×8760 + 0.10×87600] = 8.74 × 10-3

PT-101C: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (1.05 × 10-6/2) × [0.90×8760 + 0.10×87600] = 8.74 × 10-3

Beta = 0.1 (source: Manual) Formula: PFD_2oo3 = (1-β)×12×PFD_ch_UD² + β×PFD_ch_UD = (1 - 0.1) × 12 × 8.74 × 10-3² + 0.1 × 8.74 × 10-3 Subsystem PFDavg = 1.70 × 10-3

### Logic Solver (1oo2)

| Instrument Tag | λD | DC | PTC | TI (hrs) | LT (hrs) | λDU | λDD | PFD_ch_UD | PFD_ch_DD | PFD_ch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LS-101A | 7.10 × 10-8 | 99% | 100% | 8,760 | 87,600 | 7.10 × 10-10 | 7.03 × 10-8 | 3.11 × 10-6 | 5.62 × 10-7 | 3.67 × 10-6 |
| LS-101B | 7.10 × 10-8 | 99% | 100% | 8,760 | 87,600 | 7.10 × 10-10 | 7.03 × 10-8 | 3.11 × 10-6 | 5.62 × 10-7 | 3.67 × 10-6 |

LS-101A: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (7.10 × 10-10/2) × [1.00×8760 + 0.00×87600] = 3.11 × 10-6

LS-101B: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (7.10 × 10-10/2) × [1.00×8760 + 0.00×87600] = 3.11 × 10-6

Beta = 0.02 (source: Manual) Formula: PFD_1oo2 = (1-β)×PFD_ch_UD² + β×PFD_ch_UD = (1 - 0.02) × 3.11 × 10-6² + 0.02 × 3.11 × 10-6 Subsystem PFDavg = 6.22 × 10-8

### Final Elements (1oo2)

| Instrument Tag | λD | DC | PTC | TI (hrs) | LT (hrs) | λDU | λDD | PFD_ch_UD | PFD_ch_DD | PFD_ch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| XV-101A | 5.00 × 10-7 | 0% | 85% | 8,760 | 87,600 | 5.00 × 10-7 | 0 | 5.15 × 10-3 | 0 | 5.15 × 10-3 |
| XV-101B | 5.00 × 10-7 | 0% | 85% | 8,760 | 87,600 | 5.00 × 10-7 | 0 | 5.15 × 10-3 | 0 | 5.15 × 10-3 |

XV-101A: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (5.00 × 10-7/2) × [0.85×8760 + 0.15×87600] = 5.15 × 10-3

XV-101B: PFD_ch_UD = (λDU/2) × [PTC×TI + (1−PTC)×LT] = (5.00 × 10-7/2) × [0.85×8760 + 0.15×87600] = 5.15 × 10-3

Beta = 0.1 (source: Manual) Formula: PFD_1oo2 = (1-β)×PFD_ch_UD² + β×PFD_ch_UD = (1 - 0.1) × 5.15 × 10-3² + 0.1 × 5.15 × 10-3 Subsystem PFDavg = 5.38 × 10-4

SIF Total PFDavg Calculation PFDavg_SIF = PFDavg_sensor + PFDavg_logic + PFDavg_final = 1.70 × 10-3 + 6.22 × 10-8 + 5.38 × 10-4 = 2.24 × 10-3

# 7. Results

## SIF-001

| Subsystem | Architecture | Beta Used | PFDavg | Contribution % |
| --- | --- | --- | --- | --- |
| Sensors | 2oo3 | 0.1 | 1.70 × 10-3 | 76% |
| Logic Solver | 1oo2 | 0.02 | 6.22 × 10-8 | 0% |
| Final Elements | 1oo2 | 0.1 | 5.38 × 10-4 | 24% |

Total PFDavg: 2.24 × 10-3 Achieved SIL: SIL 2 — Hardware Target SIL: SIL 2 Verification Result: PASS

Sensors contributes 76% of total PFDavg. Consider reducing proof test interval or increasing diagnostic coverage on the sensors to improve overall SIF performance.

# 8. Architectural Constraint (IEC 61508 Route 1H)

The following table presents the architectural constraint assessment per IEC 61508-2 Table 3 (Type A) and Table 4 (Type B). The hardware fault tolerance (HFT) is derived from the voting architecture. The constraint SIL is the maximum SIL claimable from hardware architecture and SFF.

## SIF-001

| Subsystem | Architecture | HFT | Component Type | SFF (%) | Constraint SIL |
| --- | --- | --- | --- | --- | --- |
| Sensors | 2oo3 | 1 | Type B | 72% | SIL 2 |
| Logic Solver | 1oo2 | 1 | Type B | 99% | SIL 3 |
| Final Elements | 1oo2 | 1 | Type A | 92% | SIL 3 |

The overall architectural constraint is SIL 2, limited by sensors. This is the maximum SIL claimable from hardware architecture and SFF per IEC 61508-2.

# 9. Systematic Capability Assessment

Systematic capability (SC) is the third barrier in the IEC 61508 three-barrier SIL verification model. Each SIF element must demonstrate a systematic capability commensurate with the target SIL. SC ratings are typically established through IEC 61508 certification, prior use evidence, or engineering assessment.

## SIF-001

| Instrument Tag | Subsystem | Declared SC | Evidence Basis |
| --- | --- | --- | --- |
| PT-101A | Sensors | SC 2 | Manufacturers Safety Manual |
| PT-101B | Sensors | SC 2 | Manufacturers Safety Manual |
| PT-101C | Sensors | SC 2 | Manufacturers Safety Manual |
| LS-101A | Logic Solver | SC 2 | Manufacturers Safety Manual |
| LS-101B | Logic Solver | SC 2 | Manufacturers Safety Manual |
| XV-101A | Final Elements | SC 2 | Manufacturers Safety Manual |
| XV-101B | Final Elements | SC 2 | Manufacturers Safety Manual |

### Subsystem SC Summary

| Subsystem | Architecture | Subsystem SC | Basis |
| --- | --- | --- | --- |
| Sensors | 2oo3 | SC 3 | SC 3 (synthesised from 3 × SC 2) — engineer confirmed sufficient independence (IEC 61508 Clause 7.4.7) |
| Logic Solver | 1oo2 | SC 2 | Minimum of channel SC values |
| Final Elements | 1oo2 | SC 2 | Minimum of channel SC values |

SC synthesis applied to Sensors — engineer has confirmed sufficient independence between channels.

The minimum systematic capability declared across all SIF elements is SC 2. This meets the target SIL of SIL 2. The engineer of record is responsible for ensuring appropriate evidence is documented for each declared SC rating.

# 10. Assumptions and Limitations

The following assumptions and limitations apply to all calculations in this report. The engineer of record is responsible for confirming each assumption is appropriate for the specific installation.

- Constant failure rate assumed (IEC 61508 useful-life period assumption). Applicable to electronic and electromechanical devices in the useful-life phase.

- Low demand mode: demand rate << 1/TI. The engineer must confirm this condition is satisfied for each SIF.

- Subsystem independence assumed. No cross-subsystem common cause failures are modelled.

- Single beta factor model. The beta factor applies uniformly to all channels in a redundant subsystem. Partial CCF events are not distinguished.

- Simplified equations from IEC 61508-6 Annex B. For SIL 3 claims, an independent Markov or fault tree analysis is recommended as a cross-check.

- Arithmetic mean used for mixed-channel redundant subsystems. For channel failure rate ratios > 5:1, verify by hand calculation.

- The PFDavg calculation uses the formula PFD_ch_UD = (λDU/2)×[PTC×TI+(1−PTC)×LT]. Failures caught by the proof test accumulate over the proof test interval TI. Residual failures not caught by the proof test accumulate over the mission time LT. The engineer is responsible for confirming both the stated PTC is achievable with the defined test procedure, and that the stated mission time is appropriate for the installation.

- Detected failure approximation PFD_ch_DD = λDD × MTTR is valid when MTTR << TI (recommended: MTTR < TI/10).

- No systematic failure modelling. This report addresses random hardware failures only. IEC 61511 requires separate assessment of systematic failure avoidance and management.

- Mission time (LT) represents the design life of the safety system. Residual dangerous failures not caught by proof testing accumulate over this period. The engineer must confirm the stated mission time is appropriate for the installation and that systematic review or replacement occurs at end of mission life.

- 2oo2 architecture: no independent CCF additive term. System fails on single-channel failure; CCF probability is subsumed within the independent channel terms.

- 2oo3 architecture: for identical channels, PFD_2oo3 > PFD_1oo2. This is mathematically correct per IEC 61508-6 Annex B. 2oo3 is typically selected for availability reasons, not to reduce PFDavg.

# 11. Scope of This Verification

SCOPE OF THIS VERIFICATION This report presents the results of a Safety Integrity Level (SIL) verification calculation for the Safety Instrumented Functions listed in Section 1. The verification has been performed in accordance with the simplified calculation methods of IEC 61511, low-demand mode. This report demonstrates that the hardware reliability of the specified SIF architectures, expressed as average probability of dangerous failure on demand (PFDavg), meets the target SIL for each function as defined in Section 1. This report does NOT constitute: • A complete functional safety assessment • A safety requirements specification • An assessment of systematic failure avoidance or management • A confirmation that the demand rate satisfies the low-demand assumption • A proof test procedure or proof test adequacy assessment • A management of change assessment The results presented are valid subject to the assumptions in Section 9. The engineer of record is responsible for confirming all assumptions are appropriate for the specific installation. Engineer: Sample Engineer Date: 22 March 2026 Revision: Rev 0

# 12. Conclusion

## SIF-001

This report presents the SIL verification for SIF-001: High Pressure Trip.

### THREE-BARRIER VERIFICATION SUMMARY

| Barrier | Description | Achieved | Result |
| --- | --- | --- | --- |
| 1 | Random hardware reliability (PFDavg) | SIL 2 | PASS |
| 2 | Architectural constraint (IEC 61508 Route 1H) | SIL 2 | PASS |
| 3 | Systematic capability | SC 2 | PASS |
|  | Overall result (minimum of three barriers) | SIL 2 | PASS |

Overall verification result: PASS — SIL 2 achieved meets or exceeds target SIL 2